## Industrial Systems
Prescriptive worksheets are no longer required to submit Retrofit incentive applications in the 2021-2024 Conservation and Demand Management Framework. This is an optional worksheet, made available to assist Retrofit applicants with calculating incentives
Version 7.0 - 2021 - 2024 CDM Framework Retrofit Program - Industrial Systems Eligible Measures Worksheet - April 8, 2024
Disclaimer: This worksheet made available by the IESO to Participants and Applicant Representatives under the Retrofit Program is for informational purposes only and intended to serve as a tool to aid with the calculation of estimated Participant Incentive and savings values, which may differ from the actual values that are calculated within the Retrofit Portal. This worksheet and any values that are calculated using this worksheet, including any automatically-populated values, are not intended to be final or binding on the IESO and are subject to the terms and conditions of the applicable Program Requirements and form of Participant Agreement. In the event and to the extent of any conflict or inconsistency between the values calculated using this worksheet and those calculated within the Retrofit Portal, the values in the Retrofit Portal will prevail. The IESO makes no guarantees, representations or warranties, express or implied, with respect to the accuracy, reliability, sufficiency, or completeness of this worksheet, including any results that may be obtained as a result of the use of the information provided herein, and expressly disclaims any and all liability associated therewith (whether arising under contract, common-law or equitable principles) and any express or implied warranties related to the use of this worksheet or its suitability for any particular purpose. The IESO shall not be held liable for any claims, actions, causes of action, demands, judgments, losses or damages whatsoever (including any direct, indirect, consequential, ‘lost profit’ damages or other damages), and any legal costs or other expenses arising out of or resulting from any inaccuracies, errors or omissions, use, misuse or reliance on the worksheet, whether in whole or in part. For greater certainty, this worksheet does not constitute ‘advice’ that should be relied upon. Participants and Applicant Representatives are encouraged to obtain their own independent business, technical and legal advice prior to submitting an Application to the Retrofit Program.
PROCESS CHILLERS
Eligibility Criterias: 1. This incentive is only applicable to systems used for process cooling. 2. Must have a rated kW/ton for the Full Load (FL) efficiency that is less than the qualifying efficiency. 3. Efficiency rating must be based on AHRI Standard 550/590 (I-P)-2018 for full-load conditions. 4. Must qualify for either ASHRAE 90.1-2016 Table 6.8.1-3 Path A or B efficiency. 5. Efficiency incentive is based on efficiency rating above the minimum efficiency level. 6. Refrigerant must comply with local codes and authorities having jurisdiction. 7. The AHRI net capacity value should be used to determine the chiller tonnage. 8. Redundant chillers are not eligible for incentives 9. The proposed process chiller must operate at least 5,700 hours per year to qualify. 10. The qualifying incentive for maximum equipment capacity is equal to or less than 1,000 tons.
Equipment Type | Assumed Base Case* | FL Efficiency of Base Case Unit | FL Efficiency of Unit Installed | FL Efficiency Improvement Below Assumed Base Case | Unit Size (tons) | Quantity | Participant Incentive ($/ton/0.01 kW/ton FL Improvement) | Total Participant Incentive
Water-cooled, Electrically Operated, Positive Displacement | <75 tons ≤0.750 kW/ton FL | 0.75 |  | 0 |  |  | 120 | 0
| ≥75 tons and <150 tons ≤0.720 kW/ton FL | 0.72 |  | 0 |  |  | 120 | 0
| ≥150 tons and <300 tons ≤0.660 kW/ton FL | 0.66 |  | 0 |  |  | 120 | 0
| ≥300 tons and <600 tons ≤0.610 kW/ton FL | 0.61 |  | 0 |  |  | 120 | 0
| ≥600 tons ≤0.560 kW/ton FL | 0.56 |  | 0 |  |  | 120 | 0
Water-cooled, Electrically Operated, Centrifugal | <75 tons ≤0.610 kW/ton FL | 0.61 |  | 0 |  |  | 120 | 0
| ≥75 tons and <150 tons ≤0.610 kW/ton FL | 0.61 |  | 0 |  |  | 120 | 0
| ≥150 tons and <300 tons ≤0.560 kW/ton FL | 0.56 |  | 0 |  |  | 120 | 0
| ≥300 tons and <600 tons ≤0.560 kW/ton FL | 0.56 |  | 0 |  |  | 120 | 0
| ≥600 tons ≤0.560 kW/ton FL | 0.56 |  | 0 |  |  | 120 | 0
* The assumed base case is based on O.Reg.509/18 Schedule 4 Section 21 Prescribed Efficiency Standard Table 6.8.1-3 of ASHRAE 90.1-2016 Energy Standard for Building Except Low-Rise Residential Buildings. Only Path A is shown in table below.
Note: The Eligible Measures Lists and Eligible Measures Worksheets are based on assumptions and are subject to change and the incentive amounts do not include HST or other applicable taxes.
INJECTION MOLDING MACHINE
Eligibility Criterias: 1. The incentive is available for installation of hybrid or all-electric injection moulding machines. 2. Hybrid machines are defined as using both servo and hydraulic motors for different functions in the same machine. 3. The new injection moulding machines must be screw type and driven by servo motors. 4. The proposed injection moulding machine must operate at least 6,000 hours per year to qualify. 5. Replacement of existing electric or hybrid injection moulding machines do not qualify. 6. Incentive is based on the new machine’s clamping tonnage.
[5 empty] | Rated Clamping tons | Quantity | Participant Incentive ($/Rated Clamping ton) | Total Participant Incentive
Replacement of an existing hydraulic injection moulding machine with all electric injection moulding machine | [6 empty] | 200 | 0
Replacement of an existing hydraulic injection moulding machine with a hybrid injection moulding machine. | [6 empty] | 100 | 0
|  |  |  | TOTAL PARTICIPANT INCENTIVE REQUESTED: |  |  |  | 0
PROJECT COST BREAKDOWN
Costs which are eligible to be included in determining applicable Participant Incentives must be costs of 3rd party suppliers directly related to the procurement and implementation of the Eligible Measures and are limited to the following:
1. Estimated costs of the equipment purchased and installed
2. Estimated costs of labour for the installation of the equipment by suppliers
3. Estimated costs to dispose of or decommission the replaced equipment
TOTAL ELIGIBLE COSTS FOR THE PROJECT: | [7 empty] | 0
For certainty, costs which are not eligible to be included in Eligible Costs include:
(i) any costs that are not third party costs or that are internal costs of the Participant, including costs of the Participant’s labour, service, administration or overhead;
(ii) financing costs of the Participant;
(iii) related insurance costs of the Participant;
(iv) costs associated with post-installation maintenance or service contracts;
(v) costs of spare parts, spare equipment or other inventories;
(vi) purchase or lease of tools for installation of equipment;
(vii) HST; or
(viii) a portion of the costs of Eligible Measures that have been or will be received from financial incentives generally funded by energy ratepayers or tax payers in the Province of Ontario
1. Total Calculated Participant Incentive | [7 empty] | 0
2. Maximum Allowable Participant Incentive (50% of Total Eligible Costs for the Project) | [7 empty] | 0
3. Estimated Participant Incentive Amount (based on lesser of 50% of Total Eligible Costs for the Project or Total Calculated Participant Incentive) | [7 empty] | 0
Name of Applicant:
Company Name:
Building Address:

## Accessibility Disclaimer
This is a locked, fillable form and not all of the content in this document may be captured by a screen-reading device. If you require additional assistance to complete and submit this form, please contact retrofit@ieso.ca

## Version Control (hidden)
FALSE | 7
Month | April
Day | 8
Year | 2024
Make sure to update the version number on the footer as there is no Excel function that can currently do this automatically

## Revision History (hidden)
Version Number | Date | Details
1 | 2021-01-04 | 2021-2024 CDM Framework Release
2 | 2021-04-08 | Added New Tiers for 300-450, 450-600 Tons Water Cooled Chillers
3 | 2022-04-08 | Converted to Multi-Input Prescriptive Measure ($/IPLV Improverment per Ton)
4 | 2022-10-12 | Changed from 'Tons' to 'tons' to be consistent with ASHRAE Standards
5 | 2023-05-17 | Revised Disclaimer
6 | 2023-10-30 | New Incentives
7 | 2024-04-08 | Injection Molding Machines Minimum Operating Hours changed from 8,000 to 6,000 as recommended by Clearesult