## Sheet1
1. Project Description and Methodology
Project description | What is the project?
In describing the project, it can be helpful to include the existing conditions as a reference, what is being installed or changed, the quantities involved, and any additions or controls included in the project. You can use a table such as below, create multiple tables if needed, or import a description from another file. Often existing and baseline are the same. In some cases, the baseline equipment and/or operating conditions could be different than existing. Existing and baseline may differ when existing equipment is not meeting current service needs, or the service needs are changing (e.g. facility change of use or occupancy schedules). Example: baseline is a new production line (standard efficiency) while the project is to invest in more expensive and efficient production equipment.
| Baseline Equipment and Operating Conditions | Project Equipment and Operating Conditions
Equipment type | Compressed air system | Compressed air system with VFD
Equipment unitary wattage (kW, HP, tons) | 75 HP | 100 HP
Equipment quantity | 3 | 2
Operating hours | 4500 | 4500
Controls | None | VFD
Other
Measurement Boundary | What is measured and where? For how long?
It can be helpful to show schematically what will be measured. If using a sampling approach, this should be documented. To determine the measurement approach, consider whether the load is consistent, or if it is expected to vary based on an external factor (CFM, production, etc.) State whether interactive effects may apply, and if the M&V will quantify interactions (e.g. upgrade to more efficient refrigeration equipment may increase load on space heating system in winter, and decrease load on space cooling in summer).
Sampling approach used? | Yes/No; if yes, specify how many measurements will be taken. To decide on sampling, consider whether you have: (1) a large quantity of equipments in your project, or (2) if the equipment operates on a wide range of parameters (e.g., CFM, production)
Impact on other fuels? | If the project's objective is to save electrcity, will the project substantially impact (increase or decrease) other energy forms purchased by the facility such as natural gas or biofuels? If so, the M&V plan should address how these impacts will be measured or estimated.
| Baseline Conditions | Project
Wattage (energy consumption) | Measured over two weeks to cover full range | Measured over two weeks to cover full range
CFM (variable) | Measured concurrent to above | Measured concurrent to above
Estimated or Stipulated Values | What are the assumptions (values that are used but not measured)?
This will allow a third party to follow your thought process.
It is assumed that the energy use varies with CFM. Therefore, production and operating hours are not measured. Savings will be extrapolated to a full year using past annual CFM consumption.
Anticipated Routine Adjustments | How will consumption be adjusted for reporting period conditions? What are the variables used?
It is assumed that the energy use varies with CFM; CFM data will be collected for a year following implementation of the project. Savings will be extrapolated to a full year using annual CFM data.
Non-Routine Adjustments (Static Factors) | What are the assumptions (values that are used but not measured)?
List all factors that are deemed static, and explain how they will be tracked. Explain how adjustments will be made if these factors change in the reporting period.
Static Factor | Tracking | Basis for adjustment
Process changes | Increase or reduction of CFM use for a similar production volume | If change by 10% or more, adjustment will be calculated using updated loads (CFM/ton produced).
Equipment replacement | Maintenance logs | If another component of the compressed air system is replaced, adjustments will be made based on the efficiency gains
Curtailment/Addition | Annual report | If a curtailment happens or a production line is added, the impact of these changes will be assessed and taken into account using updated loads (CFM/ton produced).
2. Energy and Demand Savings Calculations
Baseline Period Energy | How is the baseline energy calculated? How will it be adjusted?
Basic equations: | Baseline hourly kW = a x (Baseline hourly CFM) + b
Baseline Period Energy = Sum of (Baseline hourly kW) over measurement period / (Measurement Period CFM) x (Annual CFM)
Note: a and b are the baseline model coefficients, where "a" represents the slope and 'b" represents the intercept.
You can add project specific values, assumptions and justifications here. For production, replace CFM with qty/weight of units produced, for example. In cases where the baseline scenario is hypothetical or when baseline data are missing, then baseline energy may be calculated using engineering equations or simulated using commercial software. Note that the equation may look different if you are using multiple variables, e.g.: Baseline daily kW = a x (Baseline daily Temp) + b x (Production Volume) + c
Adjusted Baseline Period Energy | how is the adjusted baseline energy calculated?
Basic equation: | Adjusted Baseline hourly kW = a x (Reporting hourly CFM) + b
Adjusted Baseline Period Energy = Sum of (Adjusted Baseline hourly kW) over Reporting measurement period / (Reporting Measurement Period CFM) x (Annual CFM)
You can add project specific values, assumptions and justifications here.
Reporting Period Energy | How is the reporting energy calculated?
Basic equation: | Reporting Period Energy = Sum of (Reporting hourly kW) over Reporting measurement period / (Reporting Measurement Period CFM) x (Annual CFM)
You can add project specific values, assumptions and justifications here.
Savings Calculation | How are the savings calculated?
Basic equation: | Energy Savings = Adjusted Baseline Period Energy - Reporting Period Energy
You can add project specific values, assumptions and justifications here.
Anticipated Energy Savings | What are the anticipated energy savings?
This is calculated based on the above equations; you can enter the savings value here, so it can be compared to the actual results in the M&V Report.
Energy Savings =
Impact on Other Fuels | If expected, what are the impacts on other fuels?
State how impacts on other fuels (e.g. natural gas, biomass, propane, diesel fuel) will be measured or estimated.
Other fuels impact =
3. Optional reporting
If required by your organisation, you can track additional metrics in this section.
Cost savings | Utility bill cost savings; specifiy marginal utility rates for energy and (if applicable) demand savings Maintenance cost savings (or increased maintenance, if applicable)
Utility Cost Savings = kWh rate x kWh annual savings + kW rate x kW savings
Maintenance Cost Savings =
Annual Cost Savings = Utility Cost Savings + Maintenance Cost Savings
GHG emissions reduction
| Electricity factor (kg CO2 eq/kWh) | 0.03
| Natural gas factor (kg CO2 eq/m3) | 1.921
GHG emissions reductions = GHG Factor x Energy Savings
Simple project payback | Simple project payback (years) = Total Project Cost / Annual Cost Savings
4. Operational Verification
Once the project has been implemented, conducting an operational verification will help you prepare for savings reporting.
Complete the site verification form | Link